## Frontpage
Risk Assesment Form for Project Name
ISSUED FOR REVIEW | A |  | 21.09.2020 | ANP | RV | RV
REASON FOR ISSUE | REVISION |  | REV. DATE | PREP. BY | CHECKED | APPROVED
|  | Document Family: |  | LIST |  | No. of pages:
2
Project:
Location
Client:
Document Title: Risk Assesment Form for Project Name
Client Doc. No: |  | Doc. No.: |  |  |  | Rev. :
|  | ICP_RA_PR1291 |  |  |  | A

## Risk Assesment
Contractor |  | IC Pro OG Technologies Pte. Ltd. |  | RA Leader |  |  |  |  | Approved By |  |  |  |  | Reference Number:
Process |  |  |  | RA Member 1 |  |  |  |  | Signature
Process / Activity Location |  | Singpaore |  | RA Member 2
Original Assessment Date |  | 2020-09-17 |  | RA Member 3 |  |  |  |  | Name
Last Review Date |  | 2020-09-21 |  | RA Member 4 |  |  |  |  | Designation
Next Review Date |  |  |  | RA Member 5 |  |  |  |  | Date
Hazard Identification |  |  |  | Risk Evaluation |  |  |  | Risk Control
Ref | Work Activity | Hazard | Possible Injury/ ill-health/ Effect on Project / Operations | Existing Risk Controls | S | L | RPN | Additional Risk Controls | S | L | RPN | Implementation Person | Due Date | Remarks
1 | Clearing Space - Clearing Materials/ Air conditioner/ Power Sockets for Panel Installation | Live electric current, Falling of equipment/ material | Electrocution/ electric shock to workers, Trip/Slip, | Skilled Labour, House Keeping, follow SWP, Close supervision by site supervisor during work | 3 | 3 | 9 | 1. Use Gloves 2. Isolate the power before starting Work. 3. Proper prepration and use adequate tools | 3 | 2 | 6 | Customer Name
2 | Unpacking of the Panel and Movement of Panel from Store room to 2 Panel Room | Falling of equipment/ materials Sharp objects/ pointed edges | Multiple injuries to worker | Use appropriate trolley and get sufficient people to lift heavy load. | 4 | 2 | 8 | 1. Use of PPE while manual handling 2. Pre Check the route and make necessary arrangements for moving the materials. 3. Make adeqaute space for unpacking and keep the materials in designated area | 4 | 1 | 4 | Customer Name/ICPro
3 | Panel Installation mechanical and grouting | Generation of Dust/Noise Flying particles | Eye Injury to worker Ill health for worker inhaling dust Deafness/ NID/nuisance to worker | Safety glass/ goggles/face shield/ear plugs must be worn | 2 | 2 | 4 | 1.On site supervision by supervisor. | 2 | 1 | 2 | ICPro
4 | Cable Laying - Ethernet,Profibus,Fiber Optics Cables Laying at Height | 1.Tools or object fall from height due to mishandling, 2.Insufficient lighting, 3.Personal Fall from height 4.Overload resulting in ladder breakdown | Body injuries to worker, Bruises, knocks, or fall | Skilled Labour, Proper PPE - safety harness, shoes and helmet, Proper Barricade around the work location. Request fellow worker to assist while using ladder. Ensure the ladder is in good condition before use. | 3 | 2 | 6 | 1.On site supervision by supervisor 2.Toolbox meeting in a timely manner 3.Use of appropriate ladder based on the work height. | 3 | 1 | 3 | ICPro
5 | Power Cable Laying from UPS to Panel -Height work, Non availblity of existing Cable tray and Space in Cable tray | 1.Electrocution/ electric shock to workers | All electrical tools to be checked that there is no exposed parts -Workers to report any exposed wires -Regular toolbox meeting conducted on safety when handling electrical tools and equipment Tray Overload | Proper PPE -safety harness, shoes and helmet Regular toolbox meeting Regular inspection of tools | 4 | 2 | 8 | 1.On site supervision by supervisor. 2.Pre Study on the avaiblity of Cable trays. 3.Preprations for additional cable trays or routes if adequate cable trays are not available. | 3 | 1 | 3 | ICPro
6 | Cable Laying Mixing of Power and communication Cables on same cable tray | Electromagnetic interference on communication cables | Communciation errors | Segregation of communciation cable routing from power cable where ever possible. | 1 | 4 | 4 | 1.On site supervision by supervisor . 2.Pre Study on the avaiblity of Seprate Cable trays. 3. Preprations for additonals cable trays or routes if adequate cable trays are not avaible. | 1 | 3 | 3 | Customer Name/ICpro
7 | Panel Power cable - Wrong Termination | Electric short circuit | Electric Shock, Equipment damage | Skilled Labour, Pre Check on termination points, Continuity Check before powerup | 4 | 2 | 8 | 1.On site supervision by supervisor. 2. Cross check the wiring with Approved wiring diagram | 4 | 1 | 4 | ICPro
8 | Panel Power Up | Electric short circuit | Electric Shock, Equipment damage | Skilled Labour, Pre Check on termination points, Continuity Check before powerup | 4 | 2 | 8 | 1. On site supervision by supervisor. 2. Continuity Check. 3. LEW & Customer Name verification before powerup | 4 | 1 | 4 | Customer Name/ICPro
9 | Confirmation of Existing IOs, Field Instruments, Signal Type mismatches as updated/ AS Built documentation not avialble for existing System - 2/4 wire tranmistters, Volt free Contact for digital contacts | Wrong type of instrument connection | Injury/Asset damage Short circuit/Spark | Perform Instrument IO Signal Type verification as per MOS(Section: 9.9 RIO Panel Cable Transfer from Existing Panel to New Panel) | 4 | 4 | 16 | 1. Customer Name to Verify the field instrument compatibility/type. 2. Customer Name operation and maintenance team to monitor the field instruments affected during each signal cable transfer. 3. Approval from Customer Name instrumentation team before tranfering cables 4. Site Cable Transfer team to report any mismatches immediately and discuss the action. 5. Inaddition to ICPro Team supervision, Customer Name project team to witness the whole process of signal cable transfer from old panel to new panel. | 4 | 3 | 12 | Customer Name/ICPro
10 | Confirmation of Healty state/Good working condition of existing Loops, Field Instruments and other field devices | None | Non-availability of instrument readings after cable transfer | Prestudy of Field Devices and confirmation of good working condition SCADA, Checking terminations in field Side | 1 | 3 | 3 | Customer Name to ensure availability of resource experienced with existing installation | 1 | 3 | 3 | Customer Name
11 | Disturbance to Existing Cable during Identification/removal of Cables inside the existing panel | Unexpected Loss of signal monitoring | Loss of monitoring in SCADA for unplanned signals(IOs) | Operational Preprations for Non availbity of Data, Trouble shooting | 3 | 4 | 12 | 1. Avoid multiple techinicains to work on same panel. 2. Availabilty of System expert for troubleshooting if any required 3. Customer Name Operation team to monitor continiously from exsitng SCADA and inform any loss of monitoring on unplanned signals(IOs). 4. Inaddition to ICPro Team supervision, Customer Name project team to witness the whole process of cable identification, removal | 3 | 3 | 9 | Customer Name/ICPro
12 | Removing IO Cable - Cable breaking while removing as it is old cables | None | Longer time required for transfer of signal form old panel to new panel | Operational Preprations for Non availbity of Data, Trouble shooting | 3 | 3 | 9 | 1. Plan for additional terminal block installation in ANZ-STM-FUTURE Panel and lay new cables 2. Plan junction Box or alternate methods if the cables broke 3. Standby Spare Terminal Blocks | 2 | 2 | 4 | Customer Name/ICPro
13 | Removing IO Cable - Difficulty in removing from Cable Glands | Unexpected Loss of signal monitoring | Loss of monitoring in SCADA for unplanned signals(IOs) Cable cannot extend to New Panel | 1. Proper tools to be used for removing cables from Glands 2. Operational Preprations for Non availbity of Data, Trouble shooting | 2 | 2 | 4 | 1. If need to cut the cable , need to have a alternate plan, materils and approvals to extend the cables 2. Plan for additional terminal block installation in ANZ-STM-FUTURE Panel and lay new cables 3. Plan junction Box or alternate methods if the cables broke 4. Standby Spare Terminal Blocks | 1 | 2 | 2 | Customer Name/ICPro
14 | Cable Laying - Shortage of any core cables From existing Panel to New Panel | None | Longer time required for transfer of signal form old panel to new panel | Operational Preprations for Non availbity of Data, Trouble shooting | 3 | 3 | 9 | 1. Plan for additional terminal block installation in ANZ-STM-FUTURE Panel and lay new cables 2. Plan junction Box or alternate methods if the cables broke 3. Standby Spare Terminal Blocks | 2 | 2 | 4 | Customer Name/ICPro
15 | Effect on PLC - For Profibus Extension | Loss of Communication | Temporary work stop/loss of monitoring ofsignals(IOs) | Operational Preprations for Stoppage, Use of redudnant PLC | 2 | 2 | 4 | Plan Profibus Connection before fully Operational | 1 | 1 | 1 | Customer Name/ICPro
16 | Program Downloading to PLC in Panel. PLC to be in Stop mode for Hardware configuration changes | Loss of Communication | Temporary work stop/loss of monitoring of signals(IOs) | Operational Preprations for Stoppage, Use of redudnant PLC | 2 | 2 | 4 | Plan hardware configuration download before fully Operational | 1 | 1 | 1 | Customer Name/ICPro
17 | Panel Shutdown for Installation Purposes | Loss of Monitoring | Temporary work stop/loss of monitoring of signals(IOs) | Operational Preprations for Stoppage, Use of redudnant PLC | 4 | 3 | 12 | 1. Plan hardware configuration download before full Operational 2. Discuss with Customer Name on the operational impact and prepare local monitoring before shutdown. | 3 | 3 | 9 | Customer Name/ICPro

## Risk Matrix
Risk Matrix
Likelihood | Rare | Remote | Occasional | Frequent | Almost Certain
Severity | (1) | (2) | (3) | (4) | (5)
Catastrophic (5) | Medium (5) | Medium (10) | High (15) | High (20) | High (25)
Major (4) | Medium (4) | Medium (8) | Medium (12) | High (16) | High (20)
Moderate (3) | Low (3) | Medium (6) | Medium (9) | Medium (12) | High (15)
Minor (2) | Low (2) | Medium (4) | Medium (6) | Medium (8) | Medium (10)
Negligible (1) | Low (1) | Low (2) | Low (3) | Medium (4) | Medium (5)
Severity Categories and Description
Level | Severity | Description
1 | Catastrophic | Fatality, fatal diseases or multiple major injuries
2 | Major | Serious injuries or life-thretening occupational disease (includes ampulations, major fractures, multiple injuries, occupational cancer, acute poisoning)
3 | Moderate | Injury requiring medical treatment or ill-health leading to disability (inclusde lacerations, burns, sprains, minor fractures, dermatitis,deafness and work-realted upper limb disorders)
4 | Minor | Injury or ill health requiring first aid only (includes minor cuts and bruises,irritation, ill-health with temporary discomfort)
5 | Negligible | Not likely to cause injury or ill-health
Likelihood Categories and Description
Level | Likelihood | Description
1 | Rare | Not expected to occur but still possible.
2 | Remote | Not likely to occur under normal circumstances.
3 | Occasional | Possible or known to occur.
4 | Frequent | Common occurrence.
5 | Almost Certain | Continual or repeating experience.
Risk Tolerability
Risk Category | Region / Risk Index | Criteria
Intolerable | 15 to 25 | The consequences are unacceptable under the existing circumstances. The work or activity shall not proceed at all
Tolerable | 4 to 12 | After reasonable mitigating measures have been taken to reduce the probability or the severity of consequences, the work or activity may proceed upon endorsement from management
Acceptable | 1 to 3 | The consequence is extremely improbable or not severe enough to be of a concern